## Comprehensive Line List (hidden)
PROCESS LINE LIST
Rev. 0 |  | Prairie View - 06220003.01 | [23 empty] | 2021-07-22
Revised This Issuance | P&ID | LINE NO. | SIZE (IN) | SERVICE | SQ. NO. | SPEC | FROM | TO | SERVICE | FLOW (SCFM) |  |  | SG | AMB TEMP (F) | TEMPERATURE (F) |  | PRESSURE (PSIG) |  | TEMPERATURE (F) |  | PRESSURE (PSIG) |  |  |  | INSUL. | INSULATION MATERIAL
[10 empty] | Min | OP | Max |  |  | Min Op | Max OP | Min Op | Max OP | DESIGN | OPERATING | DESIGN | OP. | P. Test | H. TEST
| P-201 | 24"-LFG-102-SS1-1"IH | 24 | LFG | 102 | SS1 | WELLFIELD | LFG BLOWER SKID (ME-101) | LFG | 4850 | 7250 | 7250 | 0.94 | -2 to 92 | 80 | 120 | -3.4 | ATM | 150 | 120 | 33 | -3.1 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-201 | 2"-RPV-409-CS1 | 2 | RPV | 409 | CS1 | 101-PSV-301 (ME-101) | ATMOSPHERE | RPV | 0 | 7250 | 7250 | 0.94 | -2 to 92 | AMB | 120 | ATM | 14.9 | 150 | 120 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-201 | 2"-RPV-412-CS1 | 2 | RPV | 412 | CS1 | 111-PSV-301 (111-V-300) | ATMOSPHERE | RPV | 0 | 7250 | 7250 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-201 | 18"-LFG-103-SS1-2"IP | 18 | LFG | 103 | SS1 | LFG BLOWER (ME-101) | BLOWER AFTERCOOLER (101-E-200) | LFG | 0 | 7250 | 7250 | 0.94 | -2 to 92 | AMB | 291 | ATM | 9 | 150 | 120 | 33 | 9 | 36.3 | 49.5 | IP | 2" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-201 | 10"-LFG-103A-SS1-2"IP | 10 | LFG | 103A | SS1 | 18"-LFG-103-SS1-2"IP | 18"-LFG-104-SS1-2"IP | LFG | 0 | 7250 | 7250 | 0.94 | -2 to 92 | AMB | 291 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IP | 2" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-201 | 18"-LFG-104-SS1-2"IP | 18 | LFG | 104 | SS1 | BLOWER AFTERCOOLER (101-E-200) | BLOWER DISC. SCRUBBER (111-V-300) | LFG | 0 | 7250 | 7250 | 0.95 | -2 to 92 | AMB | 291 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IP | 2" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-201 | 16"-LFG-105-SS1-1"IH | 16 | LFG | 105 | SS1 | BLOWER DISC. SCRUBBER (111-V-300) | DARCO VESSELS (V-201/202) | LFG | 4739 | 7084 | 7084 | 0.95 | -2 to 92 | AMB | 291 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-201 | 1"-CD-201-SS1-1"IHT | 1 | CD | 201 | SS1 | LFG BLOWER SKID (ME-101) | 2"-CD-233-SS1-1"IHT / EXISTING SUMP | CD | 0 | 0 | 0 | 1 | -2 to 92 | 60 | 102 | -3.4 | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-201 | 1"-CD-202-SS1-1"IHT | 1 | CD | 202 | SS1 | BLOWER DISC. SCRUBBER (111-V-300) | 2"-CD-233-SS1-1"IHT / EXISTING SUMP | CD | 0 | 49 GPH | 49 GPH | 1 | -2 to 92 | 60 | 102 | -3.4 | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-201 | 16"-LFG-193-SS1 | 16 | LFG | 193 | SS1 | 16"-LFG-105-SS1-1"IH | LFG BLOWER (ME-101) | LFG | 0 | 7250 | 3625 | 0.95 | -2 to 92 | AMB | 291 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | NONE | NONE
| P-202A | 16"-LFG-105A-SS1-1"IH | 16 | LFG | 105A | SS1 | 16"-LFG-105-SS1-1"IH | DARCO VESSEL (V-201) | LFG | 2361 | 2361 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202A | 16"-LFG-108A-SS1-1"IH | 16 | LFG | 108A | SS1 | 16"-LFG-105-SS1-1"IH | DARCO VESSEL (V-202) | LFG | 2361 | 2361 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202A | 6"-RPV-424-SS1 | 6 | RPV | 424 | SS1 | DARCO VESSEL (V-201) | PSV-214 | RPV | 0 | 2370 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | NONE | NONE
| P-202A | 8"-RPV-424-CS1 | 8 | RPV | 424 | CS1 | PSV-214 | ATMOSPHERE | RPV | 0 | 2370 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202A | 6"-RPV-425-SS1 | 6 | RPV | 425 | SS1 | DARCO VESSEL (V-202) | PSV-216 | RPV | 0 | 2370 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | 9 | 36.3 | 49.5 | NONE | NONE
| P-202A | 8"-RPV-425-CS1 | 8 | RPV | 425 | CS1 | PSV-216 | ATMOSPHERE | RPV | 0 | 2370 | 2370 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202A | 16"-LFG-106-SS1-1"IH | 16 | LFG | 106 | SS1 | DARCO VESSEL (V-201) | PARTICULATE FILTER (FLT-207) | LFG | 2361 | 7084 | 7084 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | 7.5 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202A | 16"-LFG-107-SS1-1"IH | 16 | LFG | 107 | SS1 | DARCO VESSEL (V-202) | 16"-LFG-106-SS1 | LFG | 2361 | 3542 | 7084 | 0.95 | -2 to 92 | AMB | 102 | ATM | 14.9 | 150 | 102 | 33 | 7.5 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202A | 1"-CD-217-SS1-1"IHT | 1 | CD | 217 | SS1 | DARCO VESSEL (V-201) | 2"-CD-233-SS1-1"IHT | CD | 0 | Nil | Nil | 1 | -2 to 92 | 60 | 102 | -3.4 | 7.5 | 150 | 102 | 33 | 7.5 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-202A | 1"-CD-216-SS1-1"IHT | 1 | CD | 216 | SS1 | DARCO VESSEL (V-202) | 2"-CD-233-SS1-1"IHT | CD | 0 | Nil | Nil | 1 | -2 to 92 | 60 | 102 | -3.4 | 7.5 | 150 | 102 | 33 | 7.5 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-202A | 1"-CD-214-SS1-1"IHT | 1 | CD | 214 | SS1 | PARTICULATE FILTER (FLT-207) | 2"-CD-233-SS1-1"IHT | CD | 0 | Nil | Nil | 1 | -2 to 92 | 60 | 102 | -3.4 | 7 | 150 | 102 | 33 | 7 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-202A | 1"-CD-206-SS1-1"IHT | 1 | CD | 206 | SS1 | 16"-LFG-106A-SS1-1"IH | 1"-CD-217C-SS1-1"IHT | CD | 0 | Nil | Nil | 1 | -2 to 92 | 60 | 102 | -3.4 | 7 | 150 | 102 | 33 | 7 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-202A | 16"-LFG-106A-SS1-1"IH | 16 | LFG | 106A | SS1 | PARTICULATE FILTER (FLT-207) | CHILLER SKID (ME-203) | LFG | 4739 | 7084 | 7084 | 0.95 | -2 to 92 | 60 | 102 | ATM | 7 | 150 | 102 | 33 | 7 | 36.3 | 49.5 | IH | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 4"-HCR-600-CS3-1"IP | 4 | HCR | 600 | CS3 | CHILLER SKID (ME-203) | CHILLER CONDENSER (HX-204) | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 300 | 230 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 4"-HCR-601-CS3-1"IP | 4 | HCR | 601 | CS3 | CHILLER CONDENSER (HX-204) | CHILLER SKID (ME-203) | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 150 | 135 | 300 | 220 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 2"-HCR-601B-CS3-1"IP | 2 | HCR | 601B | CS3 | CHILLER CONDENSER (HX-204) | 4"-HCR-601-CS3-1"IP | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 150 | 135 | 300 | 220 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 3"-HCR-600B-CS3-1"IP | 3 | HCR | 600B | CS3 | 6"-HCR-600-CS3-1"IP | CHILLER CONDENSER (HX-204) | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 300 | 230 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 3/4"-HCR-600C-CS3-1"IP | 0.75 | HCR | 600C | CS3 | 6"-HCR-600-CS3-1"IP | CHILLER SKID (ME-203) | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 300 | 230 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 3/4"-HCR-602-CS3-1"IP | 0.75 | HCR | 602 | CS2 | 3/4"-HCR-600C-CS3-1"IP | 3"-HCR-600B-CS3-1"IP | HCR | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 300 | 230 | 330 | 450 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-202B | 1.25"-RPV-400-CS3 | 1.25 | RPV | 400 | CS3 | 3"-HCR-600-CS3-1"IP | 604-TRV-201 | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 400 | 300 | 440 | 600 | NONE | NONE
| P-202B | 1.25"-RPV-404-CS3 | 1.25 | RPV | 404 | CS3 | 3"-HCR-600B-CS3-1"IP | 604-TRV-203 | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 200 | 160 | 400 | 300 | 440 | 600 | NONE | NONE
| P-202B | 1"-CD-203-SS1-1"IHT | 1 | CD | 203 | SS1 | CHILLER SKID (ME-203) (121-V-300) | 1"-CD-203-HD2 | CD | 0 | 85.2 GPH | 85.2 GPH | 1 | -2 to 92 | 45 | 60 | -3.4 | 4.5 | 100 | 45 | 33 | 5.3 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-202B | 1.5"-RPV-420-CS1 | 1.5 | RPV | 420 | CS1 | 614-PSV-301 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 100 | 34 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 1.5"-RPV-413-CS1 | 1.5 | RPV | 413 | CS1 | 614-PSV-302 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 100 | 34 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 1"-RPV-414-CS1 | 1 | RPV | 414 | CS1 | 604-PSV-101 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 200 | 160 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 1"-RPV-416-CS1 | 1 | RPV | 416 | CS1 | 604-PSV-102 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 200 | 160 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 3/4"-RPV-417-CS1 | 0.75 | RPV | 417 | CS1 | 604-PSV-301 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 200 | 135 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 3/4"-RPV-418-CS1 | 0.75 | RPV | 418 | CS1 | 604-PSV-302 (ME-203) | 4"-RPV-408-CS1 | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 200 | 135 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 2"-RPV-419-CS1 | 2 | RPV | 419 | CS1 | 121-PSV-301 (ME-203) | ATMOSPHERE | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 100 | 45 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 4"-RPV-408-CS1 | 4 | RPV | 408 | CS1 | CHILLER RPV SUBHEADERS | ATMOSPHERE | RPV | 0 | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | By Others | 200 | 160 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-202B | 16"-LFG-109-CS3-1"IC | 16 | LFG | 109 | CS3 | CHILLER SKID (ME-203) (121-V-300) | 20"-LFG-109-CS3 | LFG | 2278 | 6835 | 6835 | 0.96 | -2 to 92 | 45 | 102 | 2 | 3.8 | 100 | 45 | 33 | 3.8 | 36.3 | 49.5 | IC | 1" ASTM C547, ARMAFLEX BLACK LAPSEAL & ALUM. JACKET | ?
| P-202B | 1/4"-LFG-119-SS8-1"IHT | 0.25 | LFG | 119 | SS8 | 16"-LFG-109-CS3-1"IC | GAS ANALYZER | LFG | 1 lpm | 1 lpm | 10 lpm | 0.96 | -2 to 92 | 60 | 100 | 1 | 3.8 | 100 | 45 | 33 | 3.8 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-203A | 20"-LFG-109-CS3 | 20 | LFG | 109 | CS3 | 16"-LFG-109-CS3-1"IC | MAIN COMPRESSORS SUBHEADERS | LFG | 6835 | 10304 | 10304 | 0.96 | -2 to 92 | 45 | 120 | 1 | 3.8 | 100 | 45 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 20"-LFG-109-CS3 | 20 | LFG | 138 | CS3 | 8"-LFG-138-CS3 | MAIN COMPRESSORS SUBHEADERS | LFG | 3470 | 3470 | 10261 | 0.96 | -2 to 92 | 45 | 102 | 1 | 3.8 | 100 | 45 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 12"-LFG-113-CS3 | 12 | LFG | 113 | CS3 | 20"-LFG-109-CS3-1"IC | MAIN COMPRESSOR (201-C-100) | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 60 | 102 | 1 | 3.8 | 100 | 62 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 12"-LFG-114-CS3 | 12 | LFG | 114 | CS3 | 20"-LFG-109-CS3-1"IC | MAIN COMPRESSOR (211-C-100) | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 60 | 102 | 1 | 3.8 | 100 | 62 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 2"-LO-700-CS3-1"IHT | 2 | LO | 700 | CS3 | MAIN COMPRESSOR (201-C-100) | MAIN COMP OIL COOLER (203-E-100) | LO | By Others | 120.4 (GPM) | 120.4 (GPM) | By Others | -2 to 92 | 60 | 234 | 175 | 300 | 300 | 234 | 250 | 205 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203A | 2"-LO-703-CS3-1"IHT | 2 | LO | 703 | CS3 | MAIN COMP OIL COOLER (203-E-100) | MAIN COMPRESSOR (201-C-100) | LO | By Others | 120.4 (GPM) | 120.4 (GPM) | By Others | -2 to 92 | 60 | 160 | 175 | 300 | 300 | 160 | 250 | 193 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203A | 2"-LO-701-CS3-1"IHT | 2 | LO | 701 | CS3 | MAIN COMPRESSOR (211-C-100) | MAIN COMP OIL COOLER (213-E-100) | LO | By Others | 120.4 (GPM) | 120.4 (GPM) | By Others | -2 to 92 | 60 | 234 | 175 | 300 | 300 | 234 | 250 | 205 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203A | 2"-LO-704-CS3-1"IHT | 2 | LO | 704 | CS3 | MAIN COMP OIL COOLER (213-E-100) | MAIN COMPRESSOR (211-C-100) | LO | By Others | 120.4 (GPM) | 120.4 (GPM) | By Others | -2 to 92 | 60 | 160 | 175 | 300 | 300 | 160 | 250 | 193 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203A | 3"-RPV-422-CS1 | 3 | RPV | 422 | CS1 | 201-PSV-101 | 3"-RPV-426-CS1 | RPV | By Others | By Others | 2576 | By Others | -2 to 92 | 175 | 234 | By Others | 300 | 100 | 234 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-203A | 3"-RPV-421-CS1 | 3 | RPV | 421 | CS1 | 211-PSV-101 | 3"-RPV-426-CS1 | RPV | By Others | By Others | 2576 | By Others | -2 to 92 | 175 | 234 | By Others | 300 | 100 | 234 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-203A | 4"-LFG-116-CS3-1"IP | 4 | LFG | 116 | CS3 | MAIN COMPRESSOR (201-C-100) | 6"-LFG-120-CS3 | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 200 | 234 | By Others | 205 | 300 | 234 | 250 | 205 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-203A | 4"-LFG-117-CS3-1"IP | 4 | LFG | 117 | CS3 | MAIN COMPRESSOR (211-C-100) | 6"-LFG-120-CS3 | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 200 | 234 | By Others | 205 | 300 | 234 | 250 | 205 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-203A | 10"-WG-164-CS3 | 10 | WG | 164 | CS3 | 20"-LFG-109-CS3-1"IC | OFF-SPEC GAS FLARE | WG | 2278 | 6835 | 6835 | 0.96 | -2 to 92 | 45 | 102 | 0 | 3.8 | 100 | 45 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 12"-LFG-115-CS3 | 12 | LFG | 115 | CS3 | 20"-LFG-109-CS3-1"IC | MAIN COMPRESSOR (221-C-100) | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 45 | 62 | 1 | 3.8 | 100 | 62 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203A | 1"-CD-227-SS1 | 1 | CD | 227 | SS1 | 20"-LFG-109-CS3 | OWS | CD | Nil | Nil | Nil | Nil | -2 to 92 | 45 | 62 | 1 | 3.8 | 100 | 62 | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-203B | 3"-RPV-426-CS1 | 3 | RPV | 426 | CS1 | MAIN COMPRESSORS PSV | ATMOSPHERE | RPV | 0 | 2576 | 2576 | 1.02 | -2 to 92 | 45 | 234 | 0 | 300 | 300 | 234 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-203B | 3"-RPV-423-CS1 | 3 | RPV | 423 | CS1 | 221-PSV-101 | 3"-RPV-426-CS1 | RPV | 0 | 2576 | 2576 | 1.02 | -2 to 92 | 45 | 234 | 0 | 300 | 300 | 234 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-203B | 2"-LO-702-CS3-1"IHT | 2 | LO | 702 | CS3 | MAIN COMPRESSOR (221-C-100) | MAIN COMP OIL COOLER (223-E-100) | LO | 120.4 (GPM) | 120.4 (GPM) | 120.4 (GPM) | 1.02 | -2 to 92 | 175 | 234 | 175 | 205 | 300 | 234 | 250 | 205 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203B | 2"-LO-705-CS3-1"IHT | 2 | LO | 705 | CS3 | MAIN COMP OIL COOLER (223-E-100) | MAIN COMPRESSOR (221-C-100) | LO | 120.4 (GPM) | 120.4 (GPM) | 120.4 (GPM) | 1.02 | -2 to 92 | 175 | 160 | 175 | 193 | 200 | 160 | 250 | 193 | 275 | 375 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-203B | 4"-LFG-118-CS3-1"IP | 4 | LFG | 118 | CS3 | MAIN COMPRESSOR (221-C-100) | 6"-LFG-120-CS3 | LFG | 858.667 | 2576 | 2576 | 1.02 | -2 to 92 | 175 | 234 | 175 | 205 | 300 | 234 | 250 | 205 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-203B | 6"-LFG-120-CS3-1"IP | 6 | LFG | 120 | CS3 | MAIN COMPRESSOR OUTLETS | AIR LIQUIDE SKID 2 (ME-402) | LFG | 3434.667 | 10304 | 10304 | 1.02 | -2 to 92 | 175 | 234 | 175 | 205 | 300 | 234 | 250 | 205 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-204 | 12"-RG-112-CS1 | 12 | RG | 112 | CS1 | AIR LIQUIDE SKID 2 (ME-402) | 20"-LFG-109-CS3-1"IC | RG | 2263 | 3470 | 3470 | 1.13 | -2 to 92 | 60 | 95 | 1 | 4 | 150 | 95 | 33 | 4 | 36.3 | 49.5 | NONE | NONE
| P-204 | 4"-PG-127-CS1 | 4 | PG | 127 | CS1 | AIR LIQUIDE SKID 2 (ME-402) | NRU FEED TANK (RCV-100) | PG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-204 | 1/4"-PG-196-SS8 | 0.25 | PG | 196 | SS8 | 4"-PG-127-CS1 | GAS ANALYZER | PG | 1 lpm | 1 lpm | 10 lpm | 0.6 | -2 to 92 | 80 | 86 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-204 | 8"-LFG-121-CS3-1"IP | 8 | LFG | 121 | CS3 | AIR LIQUIDE SKID 2 (ME-402) | HP AFTERCOOLER (201-E-200) | LFG | 6829 | 10261 | 10261 | 1.02 | -2 to 92 | 200 | 234 | 180 | 207 | 300 | 234 | 250 | 207 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-204 | 3"-LFG-128-SS3-1"IP | 3 | LFG | 128 | SS3 | 8"-LFG-121-CS3-1"IP | 8"-LFG-129-SS3 | LFG | 6829 | 10261 | 10261 | 1.02 | -2 to 92 | 200 | 234 | 180 | 207 | 300 | 234 | 250 | 207 | 275 | 375 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-204 | 8"-LFG-129-SS3 | 8 | LFG | 129 | SS3 | HP AFTERCOOLER (201-E-200) | AFTERCOOLER SCRUBBER (201-V-300) | LFG | 6829 | 10261 | 10261 | 1.02 | -2 to 92 | 200 | 120 | 180 | 205 | 150 | 102 | 250 | 205 | 275 | 375 | NONE | NONE
| P-204 | 8"-LFG-138-SS3 | 8 | LFG | 138 | SS3 | 8"-LFG-125-CS3 | 201-PV-500 | LFG | 6829 | 10261 | 10261 | 1.02 | -2 to 92 | 102 | 120 | 180 | 220 | 300 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 8"-LFG-125-SS3 | 8 | LFG | 125 | SS3 | AFTERCOOLER SCRUBBER (201-V-300) | AIR LIQUIDE SKID 1 (ME-401) | LFG | 6829 | 10261 | 10261 | 1.02 | -2 to 92 | 102 | 102 | 180 | 200 | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 8"-PG-122-CS1 | 8 | PG | 122 | CS1 | AIR LIQUIDE SKID 2 (ME-402) | AIR LIQUIDE SKID 1 (ME-401) | PG | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 10"-RG-123-CS1 | 10 | RG | 123 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | AIR LIQUIDE SKID 2 (ME-402) | RG | By Others | By Others | 3075 | By Others | -2 to 92 | By Others | 102 | By Others | By Others | 150 | 102 | 33 | 2 | 36.3 | 49.5 | NONE | NONE
| P-204 | 1/2"-PA-317-CU | 0.5 | PA | 317 | CU | AIR LIQUIDE SKID 1 (ME-401) | AIR LIQUIDE SKID 2 (ME-402) | PA | By Others | By Others |  | By Others | -2 to 92 | By Others | By Others | By Others | By Others | 150 | 80 | 150 | 100 | 165 | 225 | NONE | NONE
| P-204 | 8"-PG-130-CS1 | 8 | PG | 130 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | AIR LIQUIDE ACT 1 | PG | 3415 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | 180 | 200 | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 8"-PG-131-CS1 | 8 | PG | 131 | CS1 | AIR LIQUIDE ACT 1 | AIR LIQUIDE SKID 1 (ME-401) | PG | 3415 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | 180 | 200 | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 8"-PG-132-CS1 | 8 | PG | 132 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | AIR LIQUIDE ACT 2 | PG | 3415 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | 180 | 200 | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 8"-PG-133-CS1 | 8 | PG | 133 | CS1 | AIR LIQUIDE ACT 2 | AIR LIQUIDE SKID 1 (ME-401) | PG | 3415 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | 180 | 200 | 150 | 102 | 250 | 200 | 275 | 375 | NONE | NONE
| P-204 | 1"-CD-215-SS1 | 1 | CD | 215 | SS1 | AIR LIQUIDE SKID 2 (ME-402) | 2"-CD-219-SS1 | CD | NIL | NIL | NIL | NIL | -2 to 92 | AMB | 234 | ATM | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | NONE | NONE
| P-204 | 1"-CD-205-SS1 | 1 | CD | 205 | SS1 | AIR LIQUIDE SKID 1 (ME-401) | 2"-CD-219-SS1 | CD | NIL | NIL | NIL | NIL | -2 to 92 | AMB | 102 | ATM | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | NONE | NONE
| P-204 | 10"-WG-126-CS1 | 10 | WG | 126 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | 10"-WG-126-HD3 | WG | 908.33 | 2725 | 2725 | 1.46 | -2 to 92 | 60 | 72 | 0 | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | NONE | NONE
| P-204 | 1/4"-WG-135-SS8-1"IHT | 0.25 | WG | 135 | SS8 | 10"-WG-126-CS1 | GAS ANALYZER | WG | 1 lpm | 1 lpm | 10 lpm | 1.46 | -2 to 92 | 45 | 72 | 0 | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-204 | 3"-RPV-438-CS1 | 3 | RPV | 438 | CS1 | PSV-3A | ATMOSPHERE | RPV | 1710.3333 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | ATM | 250 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 3"-RPV-436-CS1 | 3 | RPV | 436 | CS1 | PSV-3B | ATMOSPHERE | RPV | 1710.3333 | 5131 | 5131 | 1.02 | -2 to 92 | 45 | 102 | ATM | 250 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 4"-RG-124-CS1-1"IHT | 4 | RG | 124 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | 24"-LFG-100-HD2 | RG | 0 | 0-350 | 350 | 1.02 | -2 to 92 | 45 | 102 | -3.1 | 10 | 150 | 102 | 33 | -3.1 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 5.62 WATT/FT
| P-204 | 6"-RPV-403-CS1 | 6 | RPV | 403 | CS1 | AIR LIQUIDE SKID 1 (ME-401) | ATMOSPHERE | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | 250 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 1/2"-RPV-434-SS8 | 0.5 | RPV | 434 | SS8 | AIR LIQUIDE SKID 1 (ME-401) | 6"-RPV-403-CS1 | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | 250 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 1/2"-RPV-401-SS8 | 0.5 | RPV | 401 | SS9 | AIR LIQUIDE SKID 2 (ME-402) | 6"-RPV-402-CS1 | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | 250 | 150 | 95 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 6"-RPV-402-CS1 | 6 | RPV | 402 | CS1 | AIR LIQUIDE SKID 2 (ME-402) | ATMOSPHERE | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | By Others | ATM | 250 | 150 | 95 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-204 | 1"-CD-204-SS1-1"IHT | 1 | CD | 204 | SS1 | AFTERCOOLER SCRUBBER | 2"-CD-219-SS1 | CD | 0.5 | 1.3 GPH | 1.3 GPH | 1 | -2 to 92 | 110 | 102 | 0 | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-204 | 1/2"-LO-707-CS1-1"IHT | 0.5 | LO | 707 | CS1 | AFTERCOOLER SCRUBBER | 1"-CD-204-SS1-1"IHT | LO | Nil | Nil | Nil | 0.9 | -2 to 92 | 110 | 102 | 0 | 2 | 150 | 102 | 33 | 2 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-204 | 1"-RPV-426-CS1 | 1 | RPV | 447 | CS1 | FEED DISCHARGE SCRUBBER (121-V-300) | ATMOSPHERE | RPV | By Others | By Others | By Others | By Others | -2 to 92 | By Others | 102 | ATM | 1 | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-205 | 10"-WG-126-HD3 | 10 | WG | 126 | HD3 | 10"-WG-126-CS1 | 14"-WG-126-CS1 | WG | 1108.33 | 1108.33 | 3325 | 1.46 | -2 to 92 | 45 | 72 | 0 | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-205 | 14"-WG-126-CS1 | 14 | WG | 126 | CS1 | 10"-WG-126-HD3 | FLAME ARRESTOR (FA-607) | WG | 1108.33 | 1108.33 | 3325 | 1.46 | -2 to 92 | 45 | 72 | 0 | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-205 | 3"-WG-066-CS1 | 3 | WG | 66 | CS1 | 14"-WG-126-CS1 | 14"-WG-126-CS1 | WG | 207.8125 | 415.625 | 831.25 | 1.46 | -2 to 92 | 45 | 72 | 0 | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-205 | 4"-NG-307-CS1 | 4 | NG | 307 | CS1 | NATURAL GAS | FLAME ARRESTOR (FA-107) | NG | 200 | 310 | 310 | 0.57 | -2 to 92 | 45 | 100 | 10 | 20 | 150 | 100 | 33 | 20 | 36.3 | 49.5 | NONE | NONE
| P-205 | 1/2"-NG-308-CS1 | 0.5 | NG | 308 | CS1 | 4"-NG-307-CS1 | THERMAL OXIDIZER (ME-502B) | NG | 0 | 315 | 315 | 0.57 | -2 to 92 | 45 | 100 | 10 | 20 | 150 | 100 | 33 | 15 | 36.3 | 49.5 | NONE | NONE
| P-205 | 1.5"-RPV-446-CS1 | 1.5 | RPV | 446 | CS1 | 10"-WG-126-CS1 | PSV-517 | RPV | 1108.33 | 1108.33 | 3325 | 1.46 | -2 to 92 | 45 | 72 | 0 | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-205 | 3"-RPV-446-CS1 | 3 | RPV | 446 | CS1 | PSV-517 | ATMOSPHERE | RPV | 1108.33 | 1108.33 | 3325 | 1.46 | -2 to 92 | 45 | 72 | ATM | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-206 | 20"-PG-177-CS1 | 20 | PG | 177 | CS1 | NRU VALVE SKID (ME-601) | PARTICULATE FILTER (FLT-703) | PG | 1252 | 2963 | 10618 | 0.57 | -2 to 92 | AMB | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-206 | 6"-PG-156-CS1 | 6 | PG | 156 | CS1 | NRU FEED TANK (RCV-100) | NRU VALVE SKID (ME-601) | PG | 1234.6667 | 3704 | 3704 | 0.6 | -2 to 92 | AMB | 86 | 100 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-PG-099-CS1 | 8 | PG | 099 | CS1 | NRU VALVE SKID (ME-601) | PARTICULATE FILTER (FLT-602) | PG | 778.667 | 2336 | 2336 | 0.6 | -2 to 92 | AMB | 86 | 18 | 32 | 150 | 86 | 100 | 25 | 110 | 150 | NONE | NONE
| P-206 | 8"-PG-098-CS1 | 8 | PG | 098 | CS1 | PARTICULATE FILTER (FLT-602) | INT BUFFER VESSEL (RCV-3400) | PG | 778.667 | 2336 | 2336 | 0.6 | -2 to 92 | AMB | 86 | 18 | 32 | 150 | 86 | 100 | 25 | 110 | 150 | NONE | NONE
| P-206 | 8"-PG-148-CS1 | 8 | PG | 148 | CS1 | NRU VALVE SKID (ME-601) | LIGHT PRODUCT VESSEL (RCV-2100) | PG | 778.667 | 3822 | 3822 | 0.6 | -2 to 92 | AMB | 86 | 90 | 100 | 150 | 86 | 150 | 95 | 165 | 225 | NONE | NONE
| P-206 | 8"-PG-150-CS1 | 8 | PG | 150 | CS1 | LIGHT PRODUCT VESSEL (RCV-2100) | NRU VALVE SKID (ME-601) | PG | 778.667 | 3822 | 3822 | 0.6 | -2 to 92 | AMB | 86 | 90 | 100 | 150 | 86 | 150 | 95 | 165 | 225 | NONE | NONE
| P-206 | 4"-WG-157-CS1 | 4 | WG | 157 | CS1 | NRU VALVE SKID (ME-601) | 14"-WG-126-CS1 | WG | 0 | 285 | 600 | 1.46 | -2 to 92 | AMB | 86 | 5 | 15 | 150 | 86 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-206 | 1/4"-WG-166-SS8-1"IHT | 0.25 | WG | 166 | SS8 | 4"-WG-157-CS1 | GAS ANALYZER | WG | 1 lpm | 1 lpm | 10 lpm | 1.46 | -2 to 92 | AMB | 86 | 5 | 15 | 150 | 86 | 33 | 15 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-206 | 10"-FG-158-CS1 | 10 | FG | 158 | CS1 | NRU VALVE SKID (ME-601) | 10"-FG-195-CS1 | FG | 0 | 4000 | 4000 | 0.6 | -2 to 92 | AMB | 86 | 5 | 15 | 150 | 86 | 33 | 10 | 36.3 | 49.5 | NONE | NONE
| P-206 | 10"-LFG-149-CS1 | 10 | LFG | 149 | CS1 | NRU VALVE SKID (ME-601) | ADS-1500 | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 10"-LFG-147-CS1 | 10 | LFG | 147 | CS1 | NRU VALVE SKID (ME-601) | ADS-1400 | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 10"-LFG-145-CS1 | 10 | LFG | 145 | CS1 | NRU VALVE SKID (ME-601) | ADS-1300 | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-LFG-144-CS1 | 8 | LFG | 144 | CS1 | ADS-1300 | NRU VALVE SKID (ME-601) | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-LFG-146-CS1 | 8 | LFG | 146 | CS1 | ADS-1400 | NRU VALVE SKID (ME-601) | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-LFG-052-CS1 | 8 | LFG | 052 | CS1 | ADS-1500 | NRU VALVE SKID (ME-601) | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 10"-LFG-143-CS1 | 10 | LFG | 143 | CS1 | NRU VALVE SKID (ME-601) | ADS-1200 | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 10"-LFG-141-CS1 | 10 | LFG | 141 | CS1 | NRU VALVE SKID (ME-601) | ADS-1100 | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-LFG-140-CS1 | 8 | LFG | 140 | CS1 | ADS-1100 | NRU VALVE SKID (ME-601) | LFG | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 8"-LFG-142-CS1 | 8 | LFG | 142 | CS1 | ADS-1200 | NRU VALVE SKID (ME-601) | LFG | 2416 | 3704 | 3704 | x+L121:X121 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 2"-RPV-464-CS1 | 2 | RPV | 464 | CS1 | 6"-PG-127-CS1 | PSV-100 | RPV | 1234.667 | 3704 | 3704 | 0.6 | -2 to 92 | AMB | 86 | 100 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3"-RPV-464-CS1 | 3 | RPV | 464 | CS1 | PSV-100 | ATMOSPHERE | RPV | 1234.667 | 3704 | 3704 | 0.6 | -2 to 92 | AMB | 86 | 100 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3/4"-RPV-454-CS1 | 0.75 | RPV | 454 | CS1 | 8"-PG-099-CS1 | PSV-603 | RPV | 778.667 | 2336 | 2336 | 0.6 | -2 to 92 | AMB | 86 | 18 | 32 | 150 | 86 | 100 | 25 | 110 | 150 | NONE | NONE
| P-206 | 1"-RPV-454-CS1 | 1 | RPV | 454 | CS1 | PSV-603 | ATMOSPHERE | RPV | 778.667 | 2336 | 2336 | 0.6 | -2 to 92 | AMB | 86 | 18 | 32 | 150 | 86 | 100 | 25 | 110 | 150 | NONE | NONE
| P-206 | 3"-RPV-440-CS1 | 3 | RPV | 440 | CS1 | 8"-PG-148-CS1 | PSV-2100 | RPV | 778.667 | 3822 | 3822 | 0.6 | -2 to 92 | AMB | 86 | 90 | 100 | 150 | 86 | 150 | 95 | 165 | 225 | NONE | NONE
| P-206 | 3"-RPV-430-CS1 | 3 | RPV | 430 | CS1 | 10"-LFG-145-CS1 | PSV-1300 | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3"-RPV-431-CS1 | 3 | RPV | 431 | CS1 | 10"-LFG-147-CS1 | PSV-1400 | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3"-RPV-432-CS1 | 3 | RPV | 432 | CS1 | 10"-LFG-149-CS1 | PSV-1500 | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3"-RPV-433-CS1 | 3 | RPV | 433 | CS1 | 10"-LFG-143-CS1 | PSV-1200 | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 3"-RPV-434-CS1 | 3 | RPV | 435 | CS1 | 10"-LFG-141-CS1 | PSV-1100 | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 4"-RPV-440-CS1 | 3 | RPV | 440 | CS1 | PSV-2100 | ATMOSPHERE | RPV | 2416 | 3822 | 3822 | 0.6 | -2 to 92 | AMB | 86 | 90 | 100 | 150 | 86 | 150 | 95 | 165 | 225 | NONE | NONE
| P-206 | 4"-RPV-430-CS1 | 4 | RPV | 430 | CS1 | PSV-1300 | ATMOSPHERE | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 4"-RPV-431-CS1 | 4 | RPV | 431 | CS1 | PSV-1400 | ATMOSPHERE | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 4"-RPV-432-CS1 | 4 | RPV | 432 | CS1 | PSV-1500 | ATMOSPHERE | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 4"-RPV-433-CS1 | 4 | RPV | 433 | CS1 | PSV-1200 | ATMOSPHERE | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-206 | 4"-RPV-434-CS1 | 4 | RPV | 435 | CS1 | PSV-1100 | ATMOSPHERE | RPV | 2416 | 3704 | 3704 | 0.6 | -2 to 92 | 100 | 150 | 80 | 140 | 150 | 86 | 200 | 140 | 220 | 300 | NONE | NONE
| P-207A | 3/4"-RPV-455-CS0 | 0.75 | RPV | 455 | CS1 | 20"-PG-177-CS1 | PSV-704 | RPV | 100 | 100 | 100 | 0.6 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 1"-RPV-455-CS1 | 1 | RPV | 455 | CS1 | PSV-704 | ATMOSPHERE | RPV | 100 | 100 | 100 | 0.6 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 20"-PG-177A-CS1 | 20 | PG | 177A | CS1 | PARTICULATE FILTER (FLT-703) | 20"-PG-151-CS1 | PG | 1252 | 10618 | 10618 | 0.57 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 20"-PG-151-CS1 | 20 | PG | 151 | CS1 | 20"-PG-177A-CS1 | VACUUM COMPRESSOR SUBHEADERS | PG | 2654.5 | 5309 | 5309 | 0.57 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 14"-PG-181-CS1 | 14 | PG | 181 | CS1 | 20"-PG-151-CS1 | VACUUM COMPRESSOR (CMP-701A) | PG | 2654.5 | 5309 | 5309 | 0.57 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 14"-PG-182-CS1 | 14 | PG | 182 | CS1 | 20"-PG-151-CS2 | VACUUM COMPRESSOR (CMP-701B) | PG | 2654.5 | 5309 | 5309 | 0.57 | -2 to 92 | 45 | 86 | -9.4 | 13.59 | 150 | 86 | 33 | 13.59 | 36.3 | 49.5 | NONE | NONE
| P-207A | 3"-RPV-457-CS1 | 3 | RPV | 457 | CS1 | 301-PSV-101 | 4"-RPV-438-CS1 | RPV | 2654.5 | 5309 | 5309 | 0.57 | -2 to 92 | 45 | 217 | ATM | ATM | 150 | 86 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-207A | 3"-RPV-458-CS1 | 3 | RPV | 458 | CS1 | 311-PSV-101 | 4"-RPV-438-CS1 | RPV | 2654.5 | 5309 | 5309 | 0.57 | -2 to 92 | 45 | 217 | ATM | ATM | 150 | 86 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-207A | 2"-LO-720-CS3-1"IHT | 2 | LO | 720 | CS3 | VACUUM COMPRESSOR A (301-C-100) | VACUUM COMP OIL COOLER A (303-E-100) | LO | 81 GPM | 81 GPM | 81 GPM | 0.9 | -2 to 92 | 45 | 217 | 25 | 50 | 300 | 217 | 100 | 22.6 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-207A | 2"-LO-721-CS3-1"IHT | 2 | LO | 721 | CS3 | VACUUM COMP OIL COOLER A (303-E-100) | VACUUM COMPRESSOR A (301-C-100) | LO | 81 GPM | 81 GPM | 81 GPM | 0.9 | -2 to 92 | 45 | 190 | 25 | 50 | 300 | 190 | 100 | 22.6 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-207A | 2"-LO-723-CS3-1"IHT | 2 | LO | 723 | CS3 | VACUUM COMPRESSOR B (311-C-100) | VACUUM COMP OIL COOLER B (311-E-100) | LO | 81 GPM | 81 GPM | 81 GPM | 0.9 | -2 to 92 | 45 | 217 | 25 | 50 | 300 | 190 | 100 | 22.6 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-207A | 2"-LO-722-CS3-1"IHT | 2 | LO | 722 | CS3 | VACUUM COMP OIL COOLER B (311-E-100) | VACUUM COMPRESSOR B (311-C-100) | LO | 81 GPM | 81 GPM | 81 GPM | 0.9 | -2 to 92 | 45 | 190 | 25 | 50 | 300 | 217 | 100 | 22.6 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-207A | 6"-PG-185-CS3-1"IP | 6 | PG | 185 | CS3 | VACUUM COMPRESSOR A | 10"-PG-189-CS3-1"IP | PG | 561 | 1530 | 1530 | 0.57 | -2 to 92 | 45 | 217.4 | 10 | 24.6 | 300 | 217 | 100 | 24.6 | 110 | 150 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-207A | 6"-PG-186-CS3-1"IP | 6 | PG | 186 | CS3 | VACUUM COMP OIL COOLER B | 10"-PG-189-CS3-1"IP | PG | 561 | 1530 | 1530 | 0.57 | -2 to 92 | 45 | 217.4 | 10 | 24.6 | 300 | 217 | 100 | 24.6 | 110 | 150 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-207B | 10"-PG-189-CS3-1"IP | 10 | PG | 189 | CS3 | VACUUM COMPRESSOR OUTLETS | VACUUM COMP AFTERCOOLER (301-E-200) | PG | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 217.4 | 10 | 24.6 | 300 | 217 | 100 | 24.6 | 110 | 150 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-207B | 10"-PG-152-CS3 | 10 | PG | 152 | CS3 | VACUUM COMP AFTERCOOLER (301-E-200) | VACUUM COMP DISCHARGE SEP. | PG | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 102 | 10 | 22.1 | 150 | 102 | 100 | 22.1 | 110 | 150 | NONE | NONE
| P-208A | 1/2"-LO-731-CS1-1"IHT | 0.5 | LO | 731 | CS1 | 1/2"-LO-730-CS1-1"IHT | VACUUM COMPRESSOR A (301-C-100) | LO | Nil | Nil | Nil | 0.9 | -2 to 92 | 45 | 102 | 10 | 22.1 | 150 | 102 | 100 | 22.1 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-208A | 1/2"-LO-732-CS1-1"IHT | 0.5 | LO | 732 | CS1 | 1/2"-LO-730-CS1-1"IHT | VACUUM COMPRESSOR B (311-C-100) | LO | Nil | Nil | Nil | 0.9 | -2 to 92 | 45 | 102 | 10 | 22.1 | 150 | 102 | 100 | 22.1 | 110 | 150 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-208A | 18"-PG-153-CS1 | 18 | PG | 153 | CS1 | VACUUM COMP DISCHARGE SEP (301-V-300) | INT BUFFER VESSEL (RCV-3400) | PG | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 102 | 10 | 22.1 | 150 | 102 | 100 | 22.1 | 110 | 150 | NONE | NONE
| P-208A | 18"-PG-161-CS1 | 18 | PG | 161 | CS1 | 18"-PG-153-CS1 | 18"-PG-151-CS1 | PG | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 102 | 10 | 22.1 | 150 | 102 | 100 | 22.1 | 110 | 150 | NONE | NONE
| P-208A | 4"-RPV-466-CS1 | 4 | RPV | 466 | CS1 | 6"-PG-098-CS1 | PSV-3400 | RPV | Nil | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 86 | ATM | 50 | 250 | 86 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-208A | 6"-RPV-466-CS1 | 6 | RPV | 466 | CS1 | PSV-3400 | ATMOSPHERE | RPV | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 86 | ATM | 50 | 45 | 86 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-208A | 1"-RPV-463-CS1 | 6 | RPV | 466 | CS1 | PSV-3400 | ATMOSPHERE | RPV | 1530 | 4590 | 4590 | 0.57 | -2 to 92 | 45 | 86 | ATM | 50 | 45 | 86 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-208A | 14"-PG-162-CS1 | 14 | PG | 162 | CS1 | INT BUFFER VESSEL (RCV-3400) | RECYCLE COMP./DISCHARGE SEP. | PG | 1766 | 5299 | 5299 | 0.57 | -2 to 92 | 45 | 86 | ATM | 20.6 | 150 | 86 | 100 | 20.6 | 110 | 150 | NONE | NONE
| P-208B | 10"-PG-163-CS1 | 10 | PG | 163 | CS1 | 14"-PG-162-CS1 | RECYCLE COMPRESSOR (401-C-100) | PG | 883.1667 | 2649.5 | 2649.5 | 0.57 | -2 to 92 | 45 | 86 | ATM | 20.6 | 150 | 86 | 100 | 20.6 | 110 | 150 | NONE | NONE
| P-208B | 2"-LO-706-CS3-1"IHT | 2 | LO | 706 | CS3 | RECYCLE COMPRESSOR (401-C-100) | RECYCLE COMP OIL COOLER (403-E-100) | LO | 59.6 GPM | 59.6 GPM | 59.6 GPM | 0.9 | -2 to 92 | 45 | 240.3 | 113 | 125 | 300 | 240 | 150 | 111 | 165 | 225 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-208B | 2"-LO-708-CS3-1"IHT | 2 | LO | 708 | CS3 | RECYCLE COMP OIL COOLER (403-E-100) | RECYCLE COMPRESSOR (401-C-100) | LO | 59.6 GPM | 59.6 GPM | 59.6 GPM | 0.9 | -2 to 92 | 45 | 180 | 113 | 125 | 250 | 190 | 150 | 111 | 165 | 225 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-208B | 6"-PG-165-CS3-2"IP | 6 | PG | 165 | CS3 | RECYCLE COMPRESSOR (401-C-100) | RECYCLE COMP AFTER COOLER (401-E-200) | PG | 883.1667 | 2649.5 | 5299 | 0.57 | -2 to 92 | 175 | 240 | 100 | 115 | 250 | 190 | 150 | 115 | 165 | 225 | IP | 2" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-208B | 6"-PG-170-CS3 | 6 | PG | 170 | CS3 | RECYCLE COMP AFTER COOLER (401-E-200) | RECYCLE DISCHARGE SEPARATOR (403-V-300) | PG | 883.1667 | 2649.5 | 5299 | 0.57 | -2 to 92 | 175 | 120 | 100 | 114 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208B | 1"-RPV-441-CS1 | 1 | RPV | 441 | CS1 | 401-PSV-301 | ATMOSPHERE | RPV |  | 5299 | 5299 | 0.57 | -2 to 92 | 175 | 113 | ATM | 250 | 150 | 120 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-208B | 1/2"-LO-714-CS3-1"IHT | 0.5 | LO | 714 | CS3 | RECYCLE DISCHARGE SEPARATOR (401-V-300) | RECYCLE COMPRESSOR (401-C-100) | LO | Nil | Nil | Nil | 0.9 | -2 to 92 | 45 | 120 | 113 | 113 | 150 | 120 | 150 | 111 | 165 | 225 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-208B | 6"-RG-159-CS1 | 6 | RG | 159 | CS1 | 10"-PG-169-CS1 | 14"-PG-162-CS1 | RG | 1766.3333 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208B | 10"-PG-169-CS1 | 10 | PG | 169 | CS1 | RECYCLE DISCHARGE SEPARATOR (403-V-300) | HEAVY PRODUCT VESSEL (RCV-3600) | PG | 1766.33 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208B | 3"-RPV-442-CS1 | 3 | RPV | 442 | CS1 | 401-PSV-101 | ATMOSPHERE | RPV | 1766.3333 | 5299 | 5299 | 0.57 | -2 to 92 | 120 | 240 | ATM | 250 | 250 | 190 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-208C | 3"-RPV-465-CS1 | 3 | RPV | 465 | CS1 | 6"-PG-169-CS1 | PSV-3600 | RPV | 1766.33 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 250 | 200 | 275 | 375 | NONE | NONE
| P-208C | 4"-RPV-465-CS1 | 4 | RPV | 465 | CS1 | PSV-3600 | ATMOSPHERE | RPV | 1766.33 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 250 | 200 | 275 | 375 | NONE | NONE
| P-208C | 10"-PG-160-CS1 | 10 | PG | 160 | CS1 | HEAVY PRODUCT VESSEL (RCV-3600) | 6"-PG-160-CS1 | PG | 1766.33 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208C | 6"-PG-160-CS1 | 6 | PG | 160 | CS1 | 10"-PG-160-CS1 | DEHYDRATION VESSEL (V-907) | PG | 1766.33 | 5299 | 5299 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208C | 6"-PG-180-CS1 | 6 | PG | 180 | CS1 | 10"-PG-160-CS1 | NRU VALVE SKID (ME-601) | PG | 626.3333 | 1879 | 1879 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-208C | 6"-WG-160A-CS1 | 6 | PG | 160A | CS1 | 6"-PG-160-CS1 | 10"-FG-195-CS1 | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-209A | 6"-PG-190-CS1 | 6 | PG | 190 | CS1 | 10"-PG-160-CS1 | 6"-PG-171-CS1 | PG | 1144.667 | 3434 | 3434 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-209A | 6"-PG-171-CS1 | 6 | PG | 171 | CS1 | DEHYDRATION VESSEL (V-907) | PARTICULATE FILTER (FLT-908) | PG | 1144.667 | 3434 | 3434 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-209A | 2"-RPV-437-CS1 | 2 | RPV | 437 | CS1 | DEHYDRATION VESSEL (V-907) | PSV-921 | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 45 | 120 | ATM | 150 | 150 | 120 | 200 | 150 | 220 | 300 | NONE | NONE
| P-209A | 3"-RPV-437-CS1 | 3 | RPV | 437 | CS1 | PSV-921 | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 45 | 120 | ATM | ATM | 150 | 120 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-209A | 2"-RPV-445-CS1 | 2 | RPV | 445 | CS1 | 6"-PG-171-CS1 | PSV-935 | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 45 | 120 | ATM | 150 | 150 | 120 | 150 | 97 | 165 | 225 | NONE | NONE
| P-209A | 3"-RPV-445-CS1 | 3 | RPV | 445 | CS1 | PSV-935 | ATMOSPHERE | RPV |  | 3420 | 3420 | 0.57 | -2 to 92 | 45 | 120 | ATM | ATM | 150 | 120 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-209A | 6"-PG-192-CS1 | 6 | PG | 192 | CS1 | PARTICULATE FILTER (FLT-908) | 6"-PG-194-CS3 | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 90 | 120 | 100 | 113 | 150 | 120 | 150 | 113 | 165 | 225 | NONE | NONE
| P-209B | 6"-PG-194-CS3 | 6 | PG | 194 | CS3 | 6"-PG-192-CS1 | STAGE 1 PRODUCT GAS COMPRESSOR | PG | 2239 | 3420 | 3420 | 0.57 | -2 to 92 | 90 | 120 | 80 | 97 | 150 | 120 | 150 | 97 | 165 | 225 | NONE | NONE
| P-209B | 1.5"-LO-710-CS6-1"IHT | 1.5 | LO | 710 | CS6 | STAGE 1 PRODUCT GAS COMPRESSOR (501-C-100) | STAGE 1 PRODUCT GAS OIL COOLER (503-E-100) | LO | 22.6 GPM | 22.6 GPM | 22.6 GPM | 0.9 | -2 to 92 | 200 | 229 | 300 | 334 | 300 | 229 | 400 | 330 | 440 | 600 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209B | 1.5"-LO-711-CS6-1"IHT | 1.5 | LO | 711 | CS6 | STAGE 1 PRODUCT GAS OIL COOLER | STAGE 1 PRODUCT GAS COMPRESSOR (501-C-100) | LO | 22.6 GPM | 22.6 GPM | 22.6 GPM | 0.9 | -2 to 92 | 200 | 160 | 300 | 333 | 200 | 160 | 400 | 330 | 440 | 600 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209B | 4"-PG-172-CS3-1"IP | 4 | PG | 172 | CS3 | STAGE 1 PRODUCT GAS COMPRESSOR (501-C-100) | STAGE 1 PRODUCT GAS AFTERCOOLER (501-E-200) | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 229 | 300 | 334 | 250 | 190 | 400 | 330 | 440 | 600 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-209B | 4"-PG-173-CS3 | 4 | PG | 173 | CS3 | STAGE 1 PRODUCT GAS AFTERCOOLER (501-E-200) | STAGE 1 PG DISCHARGE SEPARATOR (501-V-300) | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 80 | 120 | 300 | 333 | 150 | 120 | 400 | 330 | 440 | 600 | NONE | NONE
| P-209B | 4"-PG-174-CS3 | 4 | PG | 174 | CS3 | STAGE 1 PG DISCHARGE SEPARATOR (501-V-300) | 4"-PG-188-CS6 | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 80 | 120 | 300 | 333 | 150 | 120 | 400 | 330 | 440 | 600 | NONE | NONE
| P-209B | 4"-PG-188-CS3 | 4 | PG | 188 | CS6 | 4"-PG-174-CS3 | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | PG | 2239 | 3420 | 3420 | 0.57 | -2 to 92 |  | 120 |  | 333 | 150 | 120 | 400 | 330 | 440 | 600 | NONE | NONE
| P-209B | 1/2"-LO-716-CS6-1"IHT | 0.5 | LO | 716 | CS3 | STAGE 1 PG DISCHARGE SEPARATOR | STAGE 1 PRODUCT GAS COMPRESSOR (501-C-100) | LO | Nil | Nil | Nil | Nil | -2 to 92 | 80 | 120 | 300 | 333 | 150 | 120 | 400 | 330 | 440 | 600 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209B | 1"-RPV-410-CS1 | 1 | RPV | 410 | CS1 | 501-PSV-301 | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 80 | 120 | ATM | ATM | 150 | 120 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-209B | 4"-RG-175-CS3 | 4 | RG | 175 | CS3 | 3"-PG-174-CS3 | 6"-PG-192-CS1 | RG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 80 | 120 | 300 | 333 | 150 | 120 | 400 | 330 | 440 | 600 | NONE | NONE
| P-209C | 3"-RPV-444-CS1 | 3 | RPV | 444 | CS1 | 501-PSV-101 | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 80 | 120 | 300 | 333 | 150 | 120 | 400 | 330 | 440 | 600 | NONE | NONE
| P-209C | 1.5"-LO-726-CS6-1"IHT | 1.5 | LO | 726 | CS6 | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | STAGE 2 PRODUCT GAS OIL COOLER (703-E-100) | LO | 25.3 GPM | 25.3 GPM | 25.3 GPM | 0.9 | -2 to 92 | 200 | 247.3 | 900 | 956 | 300 | 247 | 1100 | 956 | 1210 | 1650 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209C | 1.5"-LO-727-CS6-1"IHT | 1.5 | LO | 727 | CS6 | STAGE 2 PRODUCT GAS OIL COOLER (703-E-100) | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | LO | 25.3 GPM | 25.3 GPM | 25.3 GPM | 0.9 | -2 to 92 | 120 | 170 | 900 | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209C | 0.5"-PG-179-CS6 | 0.5 | PG | 179 | CS6 | 4"-PG-174-CS6 | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | PG | Nil | Nil | Nil | 0.9 | -2 to 92 | 200 | 247.3 | 900 | 956 | 250 | 120 | 400 | 333 | 440 | 600 | NONE | NONE
| P-209C | 3"-PG-176-CS6-1"IP | 3 | PG | 176 | CS6 | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | STAGE 2 PRODUCT GAS AFTERCOOLER (701-E-200) | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | 900 | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | IP | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET
| P-209C | 3"-PG-178-CS6 | 3 | PG | 178 | CS6 | STAGE 2 PRODUCT GAS AFTERCOOLER (701-E-200) | STAGE 2 PG DISCHARGE SEPARATOR (701-V-300) | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | 900 | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | NONE | NONE
| P-209C | 1/2"-LO-728-CS6-1"IHT | 0.5 | LO | 728 | CS6 | STAGE 2 PG DISCHARGE SEPARATOR (701-V-300) | STAGE 2 PRODUCT GAS COMPRESSOR (701-C-100) | LO | Nil | Nil | Nil | Nil | -2 to 92 | 120 | 120 | 900 | 954 | 150 | 120 | 1100 | 954 | 1210 | 1650 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 4.94 WATT/FT
| P-209C | 2"-RPV-439-CS1 | 2 | RPV | 439 | CS1 | STAGE 2 PG DISCHARGE SEPARATOR (701-V-300) | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | ATM | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | NONE | NONE
| P-209C | 3"-RG-137-CS6 | 3 | RG | 137 | CS6 | 2"-PG-183-CS6 | 3"-PG-174-CS3 | RG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | 900 | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | NONE | NONE
| P-209C | 2"-RPV-435-CS1 | 2 | RPV | 435 | CS1 | 701-PSV-101 | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | ATM | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | NONE | NONE
| P-209C | 4"-PG-183-CS6 | 4 | PG | 183 | CS6 | STAGE 2 PG DISCHARGE SEPARATOR (701-V-300) | UTILITY INTERCONNECT | PG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 200 | 247 | 900 | 956 | 250 | 190 | 1100 | 956 | 1210 | 1650 | NONE | NONE
| P-210A | 0.25"-PG-134-SS8 | 0.25 | PG | 134 | SS8 | 4"-PG-183-CS6 | GAS ANALYZER | PG | 1lpm | 1lpm | 10lpm | 0.57 | -2 to 92 | 70 | 120 | 20 | 30 | 150 | 102 | 100 | 30 | 110 | 150 | NONE | NONE
| P-210A | 10"-FG-195-CS1 | 10 | FG | 195 | CS1 | 4"-PG-183-CS6 | 10"-FG-184-HD2 | FG | 0 | 3420 | 3420 | 0.57 | -2 to 92 | 62 | 120 | 1 | 2 | 150 | 102 | 33 | 1 | 36.3 | 49.5 | NONE | NONE
| P-210B | 3"-RPV-443-CS1 | 3 | RPV | 443 | CS1 | 10"-FG-195-CS1 | PSV-1081 | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 62 | 120 | 5 | 75 | 150 | 102 | 100 | 75 | 110 | 150 | NONE | NONE
| P-210B | 4"-RPV-443-CS1 | 4 | RPV | 443 | CS1 | PSV-1081 | ATMOSPHERE | RPV | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 62 | 120 | ATM | ATM | 150 | 102 | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-210B | 10"-FG-184-HD2 | 10 | FG | 184 | HD2 | 10"-FG-195-CS1 | 10"-FG-184-CS1 | FG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 62 | 120 | 1 | 15 | 150 | 94 | 33 | 10 | 36.3 | 49.5 | NONE | NONE
| P-210B | 10"-FG-184-CS1 | 10 | FG | 184 | CS1 | 10"-FG-184-HD2 | OFF-SPEC GAS FLARE (ME-1040) | FG | 1140 | 3420 | 3420 | 0.57 | -2 to 92 | 62 | 120 | 1 | 15 | 150 | 94 | 33 | 10 | 36.3 | 49.5 | NONE | NONE
| P-210B | 1"-NG-197-CS1 | 1 | NG | 197 | CS1 | NATURAL GAS | OFF-SPEC GAS FLARE (ME-1040) | NG | 0 | 1 | 2 | 0.57 | -2 to 92 | 45 | 100 | 5 | 10 | 150 | 94 | 33 | 10 | 36.3 | 49.5 | NONE | NONE
| P-213 | 2"-CD-233-SS1-1"IHT | 2 | CD | 233 | SS1 | CD LINES | 2"-CD-233-HD3 | CD | 140 GPM | 140 GPM | 140 GPM | 1 | -2 to 92 | 45 | 100 | 0 | 5 | 150 | AMB. | 33 | 9 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-213 | 2"-CD-233-HD3 | 2 | CD | 233 | HD3 | CD LINES | TO EXISTING SUMP | CD |  |  |  | 1 | -2 to 92 | 45 | 100 | 0 | 5 | 150 | AMB. | 33 | 9 | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-LO-712-SS1 | 1 | LO | 712 | SS1 | OWS-1301 | OIL DRUM TK-1306 | LO | Nil | Nil | Nil | 0.9 | -2 to 92 | 45 | 100 | ATM | ATM | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
YES | P-213 | 2"-CD-219-SS1 | 2 | CD | 219 | SS1 | CONDENSATE LINES | OWS-1301 | CD | 1.3 GPH | 1.3 GPH | 1.3 GPH | 1 | -2 to 92 | 45 | 100 | 1 | 3.8 | 150 | AMB. | 33 | 3.8 | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-CD-234-SS1 | 1 | CD | 234 | SS1 | OWS-1301 | TK-1305 | CD | 1 | 1.3 | 2 | 1 | -2 to 92 | 45 | 100 | ATM | ATM | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-CD-236-SS1 | 1 | CD | 236 | SS1 | TK-1305 | OWS PUMP (P-1303) | CD | 0 | 14.8 GPM | 14.8 GPM | 1 | -2 to 92 | 45 | 100 | ATM | ATM | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-CD-232-SS1 | 1 | CD | 232 | SS1 | OWS PUMP (P-1303) | 2"-LFG-233-SS1-1'IHT | CD | 0 | 14.8 GPM | 14.8 GPM | 1 | -2 to 92 | 45 | 100 | ATM | ATM | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-RPV-428-CS1 | 1 | RPV | 428 | CS1 | OWS-1301 | ATMOSPHERE | RPV | 0 | 0 | 0 | 1 | -2 to 92 | AMB | AMB | AMB | AMB | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-RPV-427-CS1 | 1 | RPV | 427 | CS1 | OIL DRUM | 1"-RPV-429-CS1 | RPV | 0 | 0 | 0 | 1 | -2 to 92 | AMB | AMB | AMB | AMB | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-213 | 1"-RPV-429-CS1 | 1 | RPV | 429 | CS1 | TK-1305 | 1"-RPV-428-CS1 | RPV | 0 | 0 | 0 | 1 | -2 to 92 | AMB | AMB | AMB | AMB | 150 | AMB. | 33 | ATM | 36.3 | 49.5 | NONE | NONE
| P-214 | 1/2"-PA-323-CU | 0.5 | PA | 323 | CU | 2"-PA-310-CU | OWS PUMP (P-1303) | PA | 0 | 10 | 10 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-313-CU | 0.5 | PA | 313 | CU | 2"-PA-310-CU | AIR LIQUIDE SKIDS | PA | 0 | 8 | 8 | 1 | -2 to 92 | AMB | 115 | AMB | 100 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1"-PA-314-CU | 1 | PA | 314 | CU | 2"-PA-310-CU | CHILLER SKID (ME-203) | PA | 0 | 48 | 48 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1"-PA-316-CU | 1 | PA | 316 | CU | 2"-PA-310-CU | LFG BLOWER (ME-101) | PA | 0 | 48 | 48 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1"-PA-334-CU | 1 | PA | 334 | CU | 2"-PA-310-CU | OUTLET SCRUBBER (V-103) | PA | 0 | 40 | 40 | 1 | -2 to 92 | AMB | 115 | AMB | 100 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-340-CU | 0.5 | PA | 340 | CU | 2"-PA-310-CU | NRU VALVE SKID (ME-601) | PA | 0 | 15 | 15 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 2"-PA-311-HD4 | 2 | PA | 311 | HD4 | 2"-PA-310-CU | PLANT AIR SUBHEADERS | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 2"-PA-312-CU | 2 | PA | 312 | CU | 2"-PA-311-HD4 | 1/2"-PA-318-CU | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-318-CU | 0.5 | PA | 318 | CU | 2"-PA-312-CU | SOV-602 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-319-CU | 0.5 | PA | 319 | CU | 2"-PA-312-CU | PCV-1016 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-320-CU | 0.5 | PA | 320 | CU | 2"-PA-312-CU | SOV-102 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-321-CU | 0.5 | PA | 321 | CU | 2"-PA-312-CU | TCV-106 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-322-CU | 0.5 | PA | 322 | CU | 1/2"-PA-311-HD4 | FV-301 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-324-CU | 0.5 | PA | 324 | CU | 1/2"-PA-322-CU | FCV-301 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-325-CU | 0.5 | PA | 325 | CU | 2"-PA-310-CU | 301-PV-500 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-326-CU | 0.5 | PA | 326 | CU | 1/2"-PA-314-CU | XV-252 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-327-CU | 0.5 | PA | 327 | CU | 2"-PA-310-CU | 201-PV-500 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-328-CU | 0.5 | PA | 328 | CU | 2"-PA-310-CU | 401-PV-500 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-329-CU | 0.5 | PA | 329 | CU | 2"-PA-310-CU | XV-103 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-330-CU | 0.5 | PA | 330 | CU | 2"-PA-310-CU | CV-3601B | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-331-CU | 0.5 | PA | 331 | CU | 2"-PA-310-CU | CV-3601A | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-332-CU | 0.5 | PA | 332 | CU | 2"-PA-310-CU | AV-3400A | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-335-CU | 0.5 | PA | 335 | CU | 2"-PA-310-CU | AV-3400B | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-336-CU | 0.5 | PA | 336 | CU | 2"-PA-310-CU | AV-3401 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-337-CU | 0.5 | PA | 337 | CU | 2"-PA-310-CU | AV-3601 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-338-CU | 0.5 | PA | 338 | CU | 2"-PA-310-CU | AV-3600 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-339-CU | 0.5 | PA | 339 | CU | 2"-PA-310-CU | XV-1025 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-340-CU | 0.5 | PA | 340 | CU | 2"-PA-310-CU | 501-PV-500 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-341-CU | 0.5 | PA | 341 | CU | 2"-PA-310-CU | 701-PV-500 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-342-CU | 0.5 | PA | 342 | CU | 2"-PA-310-CU | XV-1014 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-214 | 1/2"-PA-343-CU | 0.5 | PA | 343 | CU | 2"-PA-310-CU | XV-1087 | PA | 0 | NA | NA | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 2"-PA-310-CU | 2 | PA | 310 | CU | PLANT AIR COMPRESSORS (ME-1440) | PLANT AIR SUBHEADERS | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 1.5"-PA-300-CU | 1.5 | PA | 300 | CU | ME-1501A | ME-1508 | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 1.5"-PA-300A-CU | 1.5 | PA | 300A | CU | ME-1501B | 1.5"-PA-300-CU | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 2"-PA-301-CU | 2 | PA | 301 | CU | V-1505 | ME-1502 | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 1.5"-PA-353-CU | 1.5 | PA | 353 | CU | 1"-PA-301-CU | ME-1504 | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 2"-PA-302-CU | 2 | PA | 302 | CU | ME-1502 | ME-1503 | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 2"-PA-303-CU | 2 | PA | 303 | CU | ME-1503 | ME-1506 | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 1"-PA-309-CU | 1 | PA | 309 | CU | NITROGEN | 2"-PA-310-CU | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-215 | 1.5"-PA-354-CU | 1.5 | PA | 354 | CU | ME-1505 | 2"-PA-310-CU | PA | 0 | 115 | 115 | 1 | -2 to 92 | AMB | 115 | AMB | 115 | 150 | 115 | 150 | 120 | 165 | 225 | NONE | NONE
| P-219 | 4"-NG-340-HD2 | 4 | NG | 340 | HD2 | NATURAL GAS UTILITY | NATURAL GAS HEADER | NG | 0 | 312 | 312 | 0.9 | -2 to 92 | AMB | AMB | AMB | 100 | 150 | 94 | 33 | 20 | 36.3 | 49.5 | NONE | NONE
| P-220 | 1/2"-PG-136-SS8-1"IHT | 0.5 | PG | 136 | SS8 | GAS CHROMATOGRAPH | 24"-LFG-102-SS1 | PG | 1lpm | 1lpm | 10lpm | 0.9 | -2 to 92 | AMB | AMB | -3.4 | AMB | 100 | 60 | 33 | 1 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
| P-220 | 1/4"-RPV-406-SS8-1"IHT | 0.25 | PA | 406 | SS8 | GAS CHROMATOGRAPH | ATMOSPHERE | PA | 1lpm | 1lpm | 10lpm | 0.9 | -2 to 92 | AMB | AMB | AMB | AMB | 100 | 60 | 33 | 1 | 36.3 | 49.5 | IHT | 1" 850°F MF, ASTM C547, MINERAL WOOL & ALUM JACKET, HEAT TRACE: 3.42 WATT/FT
Note on N14: Dahi, Sanam: HALF FLOW OR FULL FLOW?
Note on O23: Dahi, Sanam: CONDENSATE IS MOSTLY WATER --> SG=1
Note on O24: Dahi, Sanam: CONDENSATE IS MOSTLY WATER --> SG=1
Note on O25: Dahi, Sanam: CONDENSATE IS MOSTLY WATER --> SG=1
Note on O26: Dahi, Sanam:
Note on N224: Dahi, Sanam: P-1303 air consumption.

## Manual Valves
MANUAL VALVE LIST
Rev. 0 | Prairie View 06220003.01
General Notes: Engineer to provide elevation for chain operated valves. Insulated valves require raised stem extensions. Check valves need to specify vertical flow up, vertical flow down, or horizontal orientation and sized to eliminate chatter. All lines containing a control valve or pressure regulator must have data manually entered.
Engineering Data | [24 empty] | Vendor Data
QTY | TAG | SIZE | LINE CLASS | LINE SEQ. NO. | VALVE RATING | SERVICE | TYPE | END TYPE | VALVE LOCATION | H2S | H2O | VACUUM | NORMAL OPERATING INLET PRESSURE (PSIG) | MAX OPERATING PRESSURE (PSIG) | MAX DIFFERENTIAL PRESSURE (PSI) | AMBIENT TEMP (F) | TEMP RANGE (MIN / MAX) (F) | TEMP OPERATING (F) | FLOW RANGE (MIN/MAX) (SCFM) | FLOW OPERATING (SCFM) | ELEVATION (ABOVE GRADE) | CV (MAX FLOW) | ACTUATOR TYPE | ADDITIONAL NOTES | MFR. | MODEL | Bid form Number
8 | Spare | 1/2" |  |  |  |  | Ball | THRD | In-Line | No | No | No | 120 | 115 |  | -2 to 92 | AMB / 115 | 115 | 0 / 115 | 115 |  |  |  |  | APOLLO | 7010327 | 1
5 | Spare | 1" | CU |  |  |  | Ball | THRD | In-Line | No | No | No | 9 | 9 |  | -2 to 92 | AMB / 291 | 102 | 0 / 7250 | 7250 |  |  |  |  | APOLLO | 7010527 | 2
6 | Spare | 1/2" |  |  |  |  | Ball | SW | In-Line | No | No | Yes |  | 13.59 |  | -2 to 92 | AMB / 86 | 86 | 1252 / 10618 | 2963 |  |  |  |  | SHARPE | 53034SW | 3
12 | Spare | 1/2" |  |  |  |  | Ball | SW X THRD | End of Line | No | Yes | No | 1 | 2 | 2 | -2 to 92 | 62 / 120 | 102 | 0 / 3420 | 3420 |  |  |  |  | SHARPE | 53034SW/TE | 4
8 | Spare | 1" | CS3 |  |  |  | Ball | SW X THRD | End of Line | No | No | No | 330 | 334 | 334 | -2 to 92 | 200 / 229 | 190 | 1140 / 3420 | 3420 |  |  |  |  | SHARPE | 53034SW/TE | 5
2 | Spare | 1/4" |  |  |  |  | Ball | Thrd | End of Line | No | No | No |  | 20 | 20 | -2 to 92 | 45 / 100 | 100 | 200 / 310 | 310 |  |  |  |  | SHARPE | 53034TE | 6
1 | Spare | 1/2" |  |  |  |  | Ball | THRD | End of Line | No | Yes | No | 1 | 2 | 2 | -2 to 92 | 62 / 120 | 102 | 0 / 3420 | 3420 |  |  |  |  | SHARPE | 53034TE | 7
5 | Spare | 1" | SS1 |  |  |  | Ball | SW | In-Line | Yes | Yes | No | ATM | ATM |  | -2 to 92 | 45 / 100 | AMB. | 1 / 2 | 1.3 |  |  |  | Gravity drain from OWS to Condensate Transfer Tank | SHARPE | 53036SW | 8
6 | Spare | 1" | SS1 |  |  |  | Ball | SW X Thrd | End of Line | Yes | Yes | No |  | 3.8 | 3.8 | -2 to 92 | 45 / 100 | AMB. | 1.3 GPH / 1.3 GPH | 1.3 GPH |  |  |  |  | SHARPE | 53036SW/TE | 9
3 | Spare | 1/2" |  |  |  |  | Ball | SW X THRD | In-Line | No | No | No | 956 | 956 |  | -2 to 92 | 200 / 247 | 190 | 1140 / 3420 | 3420 |  |  |  | 3000 psi 3pc Body | SHARPE | HP89-4467PGG-SW/TE | 10
3 | Spare | 1/2" |  |  |  |  | Ball | THRD | End of Line | No | No | No | 956 | 956 | 956 | -2 to 92 | 200 / 247 | 190 | 1140 / 3420 | 3420 |  |  |  | 3000 psi 3pc Body | SHARPE | HP89-4467PGG-TE | 11
2 | Spare | 1/4" |  |  |  |  | Ball | COMPRESSION FITTING | In-Line | No | No | No | 140 | 140 |  | -2 to 92 | 80 / 86 | 86 | 1 lpm / 10 lpm | 1 lpm |  |  |  |  | SWAGELOK | SS-43GS4 | 12
Note on F5: Sookhoo, Sasha: Select Line Sequential Number from drop down menu to auto-populate grey cells

## Automated Valves
AUTOMATED VALVE LIST
Rev. 0 | Prairie View 06220003.01 ( 7/22/2021)
General Notes: All electronic instruments shall possess NRTL certification. All lines containing a control valve or pressure regulator must have data manually entered.
Engineering Data | [30 empty] | Vendor Data
QTY | TAG | SIZE | LINE CLASS | LINE SEQ. NO. | VALVE RATING | SERVICE | TYPE | END TYPE | VALVE LOCATION | H2S | H2O | VACUUM | NORMAL OPERATING INLET PRESSURE (PSIG) | MAX OPERATING PRESSURE (PSIG) | MAX DIFFERENTIAL PRESSURE (PSI) | AMBIENT TEMP (F) | TEMP RANGE (MIN / MAX) (F) | TEMP OPERATING (F) | FLOW RANGE (MIN/MAX) (SCFM) | FLOW OPERATION | SPECIFIC GRAVITY | CV (MAX/MIN) | INDOOR / OUTDOOR | ACTUATOR TYPE | SIGNAL INPUT | SIGNAL OUTPUT | AREA CLASS RATING | POSITION INDICATION | DEFAULT VALVE POSITION | ADDITIONAL NOTES | MFR. | MODEL | Bid form Number
1 | Spare | 1" | CS1 | 195 | 600# | FG | Back Pressure Regulator | Flanged | In-Line Unidirectional | No | No | No | 400 | 1000 | 600 | -2 to 92 | 62 / 120 | 102 | 0 / 3420 | Back Pressure regulator | 0.57 | TBD | OUTDOOR | [6 empty] | Set Point = 400 PSIG. Sized by Fisher Valve @ CALTROL | FISHER | EZH-1727-6967664 | 13
1 | Spare | 1" | SS1 | 232 | 150# | CD | Solenoid | Thrd | In-Line Unidirectional | Yes | Yes | No | ATM | ATM | 150 | -2 to 92 | 45 / 100 | AMB. | 0 / 14.8 GPM |  | 1 | N/A | OUTDOOR | Electric on/off |  | 4-20 mA | Class 1 Div 2 Croup C & D |  | F.C. |  | MAGNATROL | F31K34SC-HDTH | 14
1 | Spare | 1.25" | CS1 | 307 | 150# | NG | Pressure Regulator | Thrd | In-Line Unidirectional | No | No | No | 20 | 25 | 5 | -2 to 92 | 45 / 100 | 100 | 200 / 310 |  | 0.57 | 11.75 / 18.22 | OUTDOOR |  |  |  | General Pupose / Non-Classified |  | F.C. | Set Point = 20 PSIG | CASHCO | D17-5P57-1H100000E | 15
Note on P6: Dahi, Sanam: set point = ≥ 1000 psig

## Instruments
Rev. 0 | Prairie View 06220003.01 ( 7/22/2021)
General Notes: All electronic instruments shall possess NRTL certification. All lines containing a control valve or pressure regulator must have data manually entered.
Engineering Data | [21 empty] | Vendor Data
DWG | TAG | SIZE | LINE SEQ. NO. | SERVICE | TYPE | CONNECTION SIZE | END TYPE | AMBIENT TEMP (F) | TEMP RANGE (MIN / MAX) (F) | PRESSURE RANGE (MIN / MAX) (PSIG) | TEMP OPERATING (F) | FLOW RANGE (MIN/MAX) | FLOW OPERATING (SCFM) | SPECIFIC GRAVITY | BETA | MAX PERMANENT PRESSURE LOSS (PSIG) | INDOOR / OUTDOOR | COMMS | SIGNAL OUTPUT | AREA CLASS RATING | ADDITIONAL NOTES | MFR. | MODEL | Bid form Number
1 | Spare | 1 - 1500 PSIG | 183 | PG | PI |  | FNPT | -2 to 92 | 200 / 247 | 900 / 956 | 190 | 1140 / 3420 | 3420 | 0.57 | N/A | N/A | OUTDOOR | None |  | Class 1 Div 2 Croup C & D |  | TRERICE | 700SS4004LA1500 | 16
1 | Spare | 0 - 1000 PSIG | 195 | FG | PI |  | FNPT | -2 to 92 | 62 / 120 | 1 / 2 | 102 | 0 / 3420 | 3420 | 0.57 | N/A | N/A | OUTDOOR | None |  | Class 1 Div 2 Croup C & D |  | TRERICE | 700SS4004LA1000 | 17
1 | Spare | 0 - 50 PSIG | 195 | FG | PI |  | FNPT | -2 to 92 | 62 / 120 | 1 / 2 | 102 | 0 / 3420 | 3420 | 0.57 | N/A | N/A | OUTDOOR | None |  | Class 1 Div 2 Croup C & D |  | TRERICE | 700SS4004LA60 | 18

## Drop Down Menu (hidden)
MANUAL VALVES DROP DOWN MENU LISTS | [6 empty] | AUTOMATED VALVES DROP DOWN MENU LISTS | [12 empty] | INSTRUMENTS DROP DOWN MENU LISTS
VALVE RATING | SERVICE | TYPE | END TYPE | LOCATION | ACTUATOR TYPE |  | VALVE RATING | SERVICE | TYPE | END TYPE | VALVE LOCATION |  | ACTUATOR TYPE | SIGNAL INPUT | SIGNAL OUTPUT | AREA CLASS | POSITION INDICATION | VALVE FAILURE POSITION |  | SERVICE | TYPE | END TYPE | SIGNAL INPUT | SIGNAL OUTPUT | AREA CLASS | IN/OUT | BETA | COMMS
1000 WOG | LFG | Butterfly | Lug | In-Line | Lever | Yes | 1000 WOG | LFG | Butterfly | Lug | In-Line Unidirectional | Yes | Pneumatic Modulating | 4-20 mA | 4-20 mA | Class 1 Div 1 Group C & D | Open/Close Limit Switches | F.O. | INDOOR | LFG | PIT | Lug | 4-20 mA | 4-20 mA | Class 1 Div 1 Group C & D | INDOOR | 0.4 | ModBus RTU (RS45)
150# | Water | Ball | Wafer | End of Line | Hand Wheel | No | 150# | Water | Ball | Wafer | In-Line Bi-Directional | No | Pneumatic on/off | 4-20 mA / HART | NA | Class 1 Div 2 Croup C & D | Position Transmitter | F.C. | OUTDOOR | Water | PT | Wafer | 4-20 mA / HART | NA | Class 1 Div 2 Croup C & D | OUTDOOR | 0.5 | ModBus TCP (Ethernet)
300# | Oil | V-port Ball | FNPT | NA | Gear Operator | NA | 300# | Oil | V-port Ball | FNPT | End of Line | NA | Electric on/off | 24VDC |  | General Pupose / Non-Classified | Position Transmitter with Open/Closed Switches | Fail In Last (F.I.L) | NA | Oil | TIT | FNPT | 24VDC |  | General Purpose / Non-Classified | NA | 0.6 | Ethernet IP (Allen Bradley - preferred)
600# | Air | Ball w/ Stem Extensions | MNPT |  | Chain Operated |  | 600# | Air | Ball w/ Stem Extensions | MNPT | NA |  | Electric Modulating | 120 VAC |  | NA | None | NA |  | Air | TT | MNPT | 120 VAC |  | NA |  | 0.65 | None
SS1 | Propane | Globe | Sweat |  | NA |  | GS1 | Natural Gas | Plug | SW |  |  | NA | NA |  |  | NA |  |  | Natural Gas | FIT | SW | NA |  |  |  | N/A | NA
SS2 | NAOH | Gate | Compression Fitting |  |  |  | SS1 | Propane | Globe | Sweat | [9 empty] | Propane | FT | Sweat
SS3 | Condensate | Needle | Butt Weld |  |  |  | SS2 | NAOH | Gate | Compression | [9 empty] | NAOH | PI | Compression
SS8 | N2 | Check | Flanged |  |  |  | SS3 | Condensate | Needle | Butt Weld | [9 empty] | Condensate | TI | Butt Weld
CU | NA | Ball Check | Sweat x Thread |  |  |  | SS8 | N2 | Check | Flanged | [9 empty] | N2 | FS | Flanged
HD1 |  | Swing Check | SW |  |  |  | CU |  | Ball Check | Sweat x Thread | [9 empty] | NA | UIT | Sweat x Thread
HD2 |  | Strainer - Cone Type | SW X Thrd |  |  |  | HD1 |  | Swing Check | SW X Thrd | [10 empty] | LT | SW X Thrd
HD3 |  | PSV | Thrd |  |  |  | HD2 |  | VTA | Thrd | [10 empty] | Moisture Analyzer | Thrd
HD4 |  | Strainer - Y-Type | COMPRESSION X THRD |  |  |  | HD3 |  | Forward Pressure Regulator | NA | [10 empty] | Oxygen Analyzer | 1/2" NPT
HD6 |  | Restriction Orifice | NA |  |  |  | HD4 |  | Back Pressure Regulator | [11 empty] | TE | 1/8" NPT
RLP1 |  | Solenoid |  |  |  |  | HD6 |  | Solenoid | [11 empty] | DPIT | NA
RLP2 |  | PCV |  |  |  |  | RLP1 |  | NA | [11 empty] | NA
RLP3 |  | Expansion Joint |  |  |  |  | RLP2 |  | Pressure Relief Valve
PV1 |  | NA |  |  |  |  | RLP3
PV2 | [6 empty] | PV1
PV3 | [6 empty] | PV2
CS25 | [6 empty] | PV3
NA | [6 empty] | CS25

## CV Sizing-PCV1076 (hidden)
CONTROL VALVE SIZING
REV | DATE | REVISION |  |  | BY | CHK | APP | PROJECT | [9 empty] | DATA SHEET |  | 1 | OF | 1
|  | FOR REVIEW | [5 empty] | CLIENT | [9 empty] | SPEC
[8 empty] | PROJECT NO. | [9 empty] | TAG
[8 empty] | ITEM |  |  | PCV-1076 | [6 empty] | DWG | P-210A
[8 empty] | CONTRACT | [9 empty] | SERVICE |  | FLARE GAS
MFR MODEL NO.
Location
Quantity / duty | [6 empty] | Quantity |  |  |  |  | 1 | Continuous |  |  | X | Standby
Location type & wind speed | [6 empty] | Outdoor |  |  |  |  | X | Indoor |  |  |  | Design wind, mph |  |  |  | 110
Site Elevation & Temperatures | [6 empty] | Elevation, ft. amsl | [5 empty] | Min. Ambient, °F |  |  | -2 | Max. Ambient, °F |  |  |  | 92
Electrical Area Class | [6 empty] | Class |  |  |  |  | 1 | Division |  |  | 2 | Group |  |  |  | D
Electrical Equipment | [6 empty] | Elec. Panels shall have UL label. All components shall be UL and/or FM Listed. | [9 empty] | Power
Sound, dBA at 3 ft | [8 empty] | Notes: |  |  |  | Applies to all equipment and piping
| Q = | GAS FLOW (SCFH) |  |  |  |  | 205200 |  | 3420 | scfm |  |  |  | Atmospheric pressure |  | 14.6 | psia
| S = | SPECIFIC GRAVITY |  |  |  |  | 0.58 |  | . |  |  |  |  | Maximum Capacity |  | 1383 | scfm
| T = | OPERATING TEMPERATURE (◦R) |  |  |  |  | 580 |  | 120 | °F
| *DP = | PRESSURE DROP ACROSS VALVE |  |  |  |  | 8 |  | 944 | Pout = | 936 | psig | [10 empty] | 31.6234
| P1 = | UPSTREAM PRESSURE (PSIA) |  |  |  |  | 958.6 |  | 479.3 | (50% of inlet pressure) |  |  |  | Case 1 |  |  |  | Case 2
| P2 = | DOWNSTREAM PRESSURE (PSIA) |  |  |  |  | 950.6 | [6 empty] | 3420 | Flow rate (SCFM) |  |  |  | Flow rate (SCFM)
| % = | % VALVE OPEN |  |  |  |  | 80% |  | (WIDE OPEN) |  |  |  |  | 120 | T (F) |  |  |  | T (F)
[14 empty] | 944 | P upstream (PSIG) |  |  |  | P upstream (PSIG)
| Downstream flow choked condition: | [5 empty] | NORMAL | [6 empty] | 936 | Pdownstream (PSIG) |  |  |  | Pdownstream (PSIG)
[14 empty] | 31.62 | Cv |  |  |  | Cv
| * : DP MUST BE LESS THAN 0.5P1. | [12 empty] | Selected Valve size |  |  |  | Selected Valve size
*: Select a valve for which the Cv falls between 20%-80% open stem travel.
| Cv = |  | 31.6234 |  |  | (CALCULATED VALVE Cv) | [16 empty] | 5.2349
| Cv Range = |  |  | 31.62
SELECTED VALVE SIZE =
Table is for Triac V-Series control valves.

## CV Sizing-PCV1063 (hidden)
CONTROL VALVE SIZING
REV | DATE | REVISION |  |  | BY | CHK | APP | PROJECT | [9 empty] | DATA SHEET |  | 1 | OF | 1
|  | FOR REVIEW | [5 empty] | CLIENT | [9 empty] | SPEC
[8 empty] | PROJECT NO. | [9 empty] | TAG
[8 empty] | ITEM |  |  | PCV-1063 | [6 empty] | DWG | P-210A
[8 empty] | CONTRACT | [9 empty] | SERVICE |  | FLARE GAS
MFR MODEL NO.
Location
Quantity / duty | [6 empty] | Quantity |  |  |  |  | 1 | Continuous |  |  | X | Standby
Location type & wind speed | [6 empty] | Outdoor |  |  |  |  | X | Indoor |  |  |  | Design wind, mph
Site Elevation & Temperatures | [6 empty] | Elevation, ft. amsl | [5 empty] | Min. Ambient, °F |  |  | -2 | Max. Ambient, °F |  |  |  | 92
Electrical Area Class | [6 empty] | Class |  |  |  |  | 1 | Division |  |  | 2 | Group |  |  |  | D
Electrical Equipment | [6 empty] | Elec. Panels shall have UL label. All components shall be UL and/or FM Listed. | [9 empty] | Power
Sound, dBA at 3 ft | [8 empty] | Notes: |  |  |  | Applies to all equipment and piping
| Q = | GAS FLOW (SCFH) |  |  |  |  | 205200 |  | 3420 | scfm |  |  |  | Atmospheric pressure |  | 14.6 | psia
| S = | SPECIFIC GRAVITY |  |  |  |  | 0.58 |  | . |  |  |  |  | Maximum Capacity |  | 1383 | scfm
| T = | OPERATING TEMPERATURE (◦R) |  |  |  |  | 580 |  | 120 | °F
| *DP = | PRESSURE DROP ACROSS VALVE |  |  |  |  | 999.5 |  | 1000 | Pout = | 0.5 | psig | [10 empty] | 3.8524
| P1 = | UPSTREAM PRESSURE (PSIA) |  |  |  |  | 1014.6 |  | 507.3 | (50% of inlet pressure) |  |  |  | Case 1 |  |  |  | Case 2
| P2 = | DOWNSTREAM PRESSURE (PSIA) |  |  |  |  | 15.1 | [6 empty] | 3420 | Flow rate (SCFM) |  |  | 3420 | Flow rate (SCFM)
| % = | % VALVE OPEN |  |  |  |  | 80% |  | (WIDE OPEN) |  |  |  |  | 120 | T (F) |  |  | 120 | T (F)
[14 empty] | 1000 | P upstream (PSIG) |  |  | 1000 | P upstream (PSIG)
| Downstream flow choked condition: | [5 empty] | CHOKED | [6 empty] | 0.5 | Pdownstream (PSIG) |  |  | 400 | Pdownstream (PSIG)
[14 empty] | 4.95 | Cv |  |  | 4.95 | Cv
| * : DP MUST BE LESS THAN 0.5P1. | [12 empty] | Selected Valve size |  |  |  | Selected Valve size
*: Select a valve for which the Cv falls between 20%-80% open stem travel.
| Cv = |  | 4.9459 |  |  | (CALCULATED VALVE Cv) | [16 empty] | 4.9459
| Cv Range = |  |  | 4.95
SELECTED VALVE SIZE =
Table is for Triac V-Series control valves.

## CV Sizing-PCV1064 (hidden)
CONTROL VALVE SIZING
REV | DATE | REVISION |  | BY | CHK | APP | PROJECT | [9 empty] | DATA SHEET |  | 1 | OF | 1
|  | FOR REVIEW |  |  |  |  | CLIENT | [9 empty] | SPEC
[7 empty] | PROJECT NO. | [9 empty] | TAG
[7 empty] | ITEM |  |  | PCV-1064 | [6 empty] | DWG | P-210A
[7 empty] | CONTRACT | [9 empty] | SERVICE |  | FLARE GAS
MFR MODEL NO.
Location
Quantity / duty | [5 empty] | Quantity |  |  |  |  | 1 | Continuous |  |  | X | Standby
Location type & wind speed | [5 empty] | Outdoor |  |  |  |  | X | Indoor |  |  |  | Design wind, mph |  |  |  | 110
Site Elevation & Temperatures | [5 empty] | Elevation, ft. amsl | [5 empty] | Min. Ambient, °F |  |  | -2 | Max. Ambient, °F |  |  |  | 92
Electrical Area Class | [5 empty] | Class |  |  |  |  | 1 | Division |  |  | 2 | Group |  |  |  | D
Electrical Equipment | [5 empty] | Elec. Panels shall have UL label. All components shall be UL and/or FM Listed. | [9 empty] | Power
Sound, dBA at 3 ft | [7 empty] | Notes: |  |  |  | Applies to all equipment and piping
| Q = | GAS FLOW (SCFH) |  |  |  | 205200 |  | 3420 | scfm |  |  |  | Atmospheric pressure |  | 14.6 | psia
| S = | SPECIFIC GRAVITY |  |  |  | 0.58 |  | . |  |  |  |  | Maximum Capacity |  | 1383 | scfm
| T = | OPERATING TEMPERATURE (◦R) |  |  |  | 580 |  | 120 | °F
| *DP = | PRESSURE DROP ACROSS VALVE |  |  |  | 200 |  | 600 | Pout = | 400 | psig | [10 empty] | 8.6142
| P1 = | UPSTREAM PRESSURE (PSIA) |  |  |  | 614.6 |  | 307.3 | (50% of inlet pressure) |  |  |  | Case 1 |  |  |  | Case 2
| P2 = | DOWNSTREAM PRESSURE (PSIA) |  |  |  | 414.6 | [6 empty] | 3420 | Flow rate (SCFM) |  |  |  | Flow rate (SCFM)
| % = | % VALVE OPEN |  |  |  | 80% |  | (WIDE OPEN) |  |  |  |  | 120 | T (F) |  |  |  | T (F)
[14 empty] | P upstream (PSIG) |  |  |  | P upstream (PSIG)
| Downstream flow choked condition: |  |  |  |  | NORMAL | [6 empty] | 400 | Pdownstream (PSIG) |  |  |  | Pdownstream (PSIG)
[13 empty] | 4.66 | Cv |  |  |  | Cv
| * : DP MUST BE LESS THAN 0.5P1. | [11 empty] | Selected Valve size |  |  |  | Selected Valve size
*: Select a valve for which the Cv falls between 20%-80% open stem travel.
| Cv = |  | 8.6142 |  | (CALCULATED VALVE Cv) | [16 empty] | 8.1649
Cv Range =
SELECTED VALVE SIZE =
Table is for Triac V-Series control valves.

## CV Sizing-PCV1052 (hidden)
CONTROL VALVE SIZING
REV | DATE | REVISION |  |  | BY | CHK | APP | PROJECT | [9 empty] | DATA SHEET |  | 1 | OF | 1
|  | FOR REVIEW | [5 empty] | CLIENT | [9 empty] | SPEC
[8 empty] | PROJECT NO. | [9 empty] | TAG
[8 empty] | ITEM |  |  | PCV-1052 | [6 empty] | DWG | P-210A
[8 empty] | CONTRACT | [9 empty] | SERVICE |  | FLARE GAS
MFR MODEL NO.
Location
Quantity / duty | [6 empty] | Quantity |  |  |  |  | 1 | Continuous |  |  | X | Standby
Location type & wind speed | [6 empty] | Outdoor |  |  |  |  | X | Indoor |  |  |  | Design wind, mph
Site Elevation & Temperatures | [6 empty] | Elevation, ft. amsl | [5 empty] | Min. Ambient, °F |  |  | -2 | Max. Ambient, °F |  |  |  | 92
Electrical Area Class | [6 empty] | Class |  |  |  |  | 1 | Division |  |  | 2 | Group |  |  |  | D
Electrical Equipment | [6 empty] | Elec. Panels shall have UL label. All components shall be UL and/or FM Listed. | [9 empty] | Power
Sound, dBA at 3 ft | [8 empty] | Notes: |  |  |  | Applies to all equipment and piping
| Q = | GAS FLOW (SCFH) |  |  |  |  | 205200 |  | 3420 | scfm |  |  |  | Atmospheric pressure |  | 14.6 | psia
| S = | SPECIFIC GRAVITY |  |  |  |  | 0.58 |  | . |  |  |  |  | Maximum Capacity |  | 1383 | scfm
| T = | OPERATING TEMPERATURE (◦R) |  |  |  |  | 580 |  | 120 | °F
| *DP = | PRESSURE DROP ACROSS VALVE |  |  |  |  | 399 |  | 400 | Pout = | 1 | psig | [10 empty] | 9.4332
| P1 = | UPSTREAM PRESSURE (PSIA) |  |  |  |  | 414.6 |  | 207.3 | (50% of inlet pressure) |  |  |  | Case 1 |  |  |  | Case 2
| P2 = | DOWNSTREAM PRESSURE (PSIA) |  |  |  |  | 15.6 | [6 empty] | 3420 | Flow rate (SCFM) |  |  |  | Flow rate (SCFM)
| % = | % VALVE OPEN |  |  |  |  | 80% |  | (WIDE OPEN) |  |  |  |  | 120 | T (F) |  |  |  | T (F)
[14 empty] | 400 | P upstream (PSIG) |  |  |  | P upstream (PSIG)
| Downstream flow choked condition: | [5 empty] | CHOKED | [6 empty] | 1 | Pdownstream (PSIG) |  |  |  | Pdownstream (PSIG)
[14 empty] | 12.1 | Cv |  |  |  | Cv
| * : DP MUST BE LESS THAN 0.5P1. | [12 empty] | Selected Valve size |  |  |  | Selected Valve size
*: Select a valve for which the Cv falls between 20%-80% open stem travel.
| Cv = |  | 12.1036 |  |  | (CALCULATED VALVE Cv) | [16 empty] | 12.1036
| Cv Range = |  |  | 12.1
SELECTED VALVE SIZE =
Table is for Triac V-Series control valves.